## Slide 1
SHEETAL
Sustainable Hydrogel-Enabled Energy Efficient Thermal Augmentation for Air-conditioning Load Reduction
Indian innovation for energy-efficient cooling.
Platinum Jubilee Innovation Challenge 2026 | IIT Kharagpur
Team MEGHDOOT
Vinay Arya · Vikash Chandra · Aman Kumar · Shivam Kumar
School of Energy Science and Engineering, IIT Kharagpur
Mentor: Dr. Chirodeep Bakli | Associate Professor, SESE, IIT Kharagpur

## Slide 2
CRITERION 1 | Problem Significance & Clarity
The Cooling Problem at IIT Kharagpur
SHEETAL | Team MEGHDOOT | IIT Kharagpur | PJIC 2026
1000+
Split AC units across IIT KGP campus
Faculty, labs, hostels
15-25%
Efficiency drop in peak summer
When demand is highest
45 °C
Peak ambient temperature (KGP)
May-June every year
Rs. Crores
Annual campus cooling cost
And growing every year
Why this problem matters:
• IIT KGP's cooling is largely served by distributed split ACs — not centralised chilled water.
• Split AC efficiency degrades in hot weather: the outdoor condenser must reject heat to increasingly hot ambient air,
forcing the compressor to work harder — and consume more electricity — precisely when cooling demand is highest.
• Replacing units is capital-intensive; most efficiency upgrades need extra energy, water, or maintenance.
• Even a 5-10% improvement across 1000+ units yields substantial cumulative savings and meaningful carbon reduction.

## Slide 3
CRITERION 1 | Problem Significance
Why Existing Approaches Fall Short
The gap that SHEETAL fills
SHEETAL | Team MEGHDOOT | IIT Kharagpur | PJIC 2026
Replace With New Units
✗ Rs. 30-60K per unit
✗ Major campus disruption
✗ Creates e-waste
✗ Not scalable
Continuous Water Spray
✗ Needs pump + piping
✗ Legionella / scaling risk
✗ High water demand
✗ Ongoing maintenance
Shade Structures / Films
✗ Marginal gain (< 3%)
✗ Can block airflow
✗ Structural load on wall
✗ No active cooling
SHEETAL (Our Innovation)
✓ Completely passive
✓ No pump / no power
✓ Retrofit in < 30 min
✓ Est. 15-20% COP gain

## Slide 4
CRITERION 2 | Originality & Creativity
SHEETAL: The Proposed Innovation
SHEETAL | Team MEGHDOOT | IIT Kharagpur | PJIC 2026
What is SHEETAL?
A PAM-LiCl hydrogel panel retrofitted onto the air intake of any split AC outdoor condenser unit.
Core mechanism:
The hygroscopic hydrogel absorbs atmospheric moisture at night and releases it via evaporation during hot daytime periods, cooling the condenser inlet air by 4-10 °C.
What makes it novel:
Applies atmospheric water harvesting + desiccant cooling principles as a zero-energy AC retrofit. No prior commercial product combines these into a passive condenser pre-cooler.
Key advantage:
Completely passive. No pump, no water supply, no external power, no structural change. Clips onto any condenser grille in under 30 minutes.

## Slide 5
CRITERION 3 | Technical Feasibility
Working Mechanism: Day & Night Cycle
SHEETAL | Team MEGHDOOT | IIT Kharagpur | PJIC 2026
DAYTIME — Evaporative Cooling Cycle
1. Hot ambient air (40-45 °C, RH 25-40%) sweeps the condenser intake.
2. Air passes through the PAM-LiCl hydrogel panel.
3. LiCl lowers the vapour pressure at the gel surface (aᵤ ≈ 0.80).
4. Moisture evaporates from gel into the airstream → latent heat absorbed.
5. Condenser inlet air temperature drops 4-10 °C.
6. Cooler air → better heat rejection → lower compressor head pressure.
7. Compressor power reduces → lower electricity draw → higher COP.
NIGHT — Autonomous Regeneration Cycle
1. Temperature drops (25-32 °C), relative humidity rises (60-80%).
2. Gel equilibrium RH ≈ 80% (for 30 wt% LiCl) → below ambient RH.
3. Atmospheric moisture flows into the gel (spontaneous adsorption).
4. PAM matrix swells, storing water for the next day's cycle.
5. No pump, no valve, no active control — fully autonomous.
6. Hydrogel is fully recharged by morning.
7. Cycle repeats: like a desert beetle, every single day.

## Slide 6
CRITERION 3 | Scientific Soundness
PAM-LiCl Hydrogel: Material Selection Rationale
SHEETAL | Team MEGHDOOT | IIT Kharagpur | PJIC 2026
Water Activity (aᵤ)
0.75-0.85 at 30 wt% LiCl (Conde 2004) Equilibrium RH = 75-85% Enables evaporation when ambient RH < 80%
Water Uptake
> 5 g water / g polymer (PAM hydrogel) Thin 3 mm panel holds enough water for 15-50 h of continuous cooling
Evaporation Rate
j ≈ 50 μg/(m²·s) (Analytical, 45°C, RH 30%) Surface cooling: 4-10 K COP improvement: ~15-20%
Self-Regeneration
Absorbs moisture from humid night air passively Cycle life: > 500 cycles (Li et al. 2018 ref.) No cartridge replacement
Synthesis & Cost
Free-radical polymerisation Low-cost: AAm + MBA + LiCl LiCl impregnation post-gelation Scalable to sheet format Est. material: Rs. 200-400/unit
References: Conde (2004), Int. J. Refrig.; Li et al. (2018), Nat. Commun.; Zhao et al. (2019), Sci. Adv.

## Slide 7
CRITERION 3 | Technical Feasibility & Scientific Soundness
Analytical Model (NTU-Effectiveness + Chilton-Colburn)
SHEETAL | Team MEGHDOOT | IIT Kharagpur | PJIC 2026

## Slide 8
CRITERION 3 | Technical Feasibility
Key Model Predictions
SHEETAL | Team MEGHDOOT | IIT Kharagpur | PJIC 2026
Condenser Inlet Temp. Drop
4.4 K
Bulk air: 45 °C → 40.6 °C (40 cm panel, u=0.35 m/s)
COP Improvement (Estimated)
~20%
Carnot-based, T_cond drop of ~5 K
Nu / Sh (Graetz Corr.)
6.2 / 6.0
Entry-length correction Re = 413, Pr = 0.69
Panel Endurance
15-50 h
3-10 mm PAM-LiCl before night recharge
Governing equations (base case: L=40 cm, H=20 mm, u=0.35 m/s, T_in=45°C, RH=30%, PAM-LiCl 30 wt%)
h_conv = Nu * k_air / H = 8.42 W/(m²K) NTU_T = h_conv * L / (G * c_p) = 0.42 T_out = T_gel + (T_in - T_gel) * exp(-NTU_T)
h_mass = Sh * D_vap / H = 9.05 mm/s NTU_m = h_mass * L / (u * H) = 0.52 omega_out = omega_gel + (omega_in - omega_gel) * exp(-NTU_m)
omega_gel = a_w(w_LiCl) * omega_sat(T_gel) j_evap = rho * h_mass * (omega_gel - omega_air) Endurance = m_water / j_evap

## Slide 9
CRITERION 5 | Prototype Quality & Development Stage
Prototype Design & Experimental Validation Plan
SHEETAL | Team MEGHDOOT | IIT Kharagpur | PJIC 2026
Technology Readiness Level
DONE Basic principles observed
DONE Technology concept formulated
TRL 3 Experimental PoC (next 2 weeks)
TRL 4 Lab-scale validation
TRL 5 Relevant environment test
TRL 6 Prototype demo in situ
TRL 7 System prototype operational
TRL 8 System complete & qualified
TRL 9 Deployment proven
Prototype & Validation Plan
Phase 1 — Hydrogel Synthesis
Synthesise PAM-LiCl sheets (30 wt% LiCl). Measure water uptake, a_w, evaporation rate at 35-45 °C in lab.
Phase 2 — Bench Channel Test
Lab-scale air channel (40x20 mm). Heater + hygrometer. Measure DeltaT and j_evap. Validate vs. analytical model.
Phase 3 — Condenser Mockup
Aluminium frame + gel panel for standard 1.5T split AC (800x550 mm face). Test fit and pressure drop.
Phase 4 — Field Trial (SESE Building)
Install on 2-3 AC units. Log compressor current, power, indoor T over 2-4 weeks. Compare with controls.
Key Metrics
DeltaT_condenser, DeltaW_compressor, COP_before vs COP_after, gel recharge time, daily water balance.

## Slide 10
CRITERION 4 | Impact Potential: Scale, Depth & Reach
How Big Can This Get?
SHEETAL | Team MEGHDOOT | IIT Kharagpur | PJIC 2026
IIT KGP Campus
~1000 split AC units
• 20% COP improvement
• 15-25% electricity saving on AC
• Meaningful carbon reduction
• Visible net-zero contribution
Indian Campuses
>1000 universities / IITs / NITs
• Millions of split AC units
• Procurement via sustainability MoU
• Replicable IIT Kharagpur model
• Central govt. green campus push
Indian Residential
300 million+ AC units in India
• World's fastest-growing AC market
• No infrastructure change needed
• Works on any split AC brand
• Affordable retrofit for all
Global South
Hot & humid tropical climates
• Maximum benefit in hot countries
• No grid power required
• Climate adaptation technology
• Aligns with SDG 7 & SDG 13

## Slide 11
CRITERION 6 | Business & Implementation Viability
Path to Deployment
SHEETAL | Team MEGHDOOT | IIT Kharagpur | PJIC 2026
Unit Economics (Estimated)
Material cost (per unit):
~Rs. 200-400
Frame + fitting hardware:
~Rs. 300-500
Total manufacturing cost:
~Rs. 500-900
Retail price (2x markup):
~Rs. 1,000-1,800
Annual electricity saving:
~Rs. 1,500-4,000
Simple payback period:
< 6 months
Panel lifespan:
> 3 years (est.)
ROI over 3 years:
4-10x investment
Go-to-Market Strategy
Phase 1 (0-6 months) — Campus Pilot
Install on 50 AC units at IIT KGP. Publish performance data. Build credibility with real numbers.
Phase 2 (6-18 months) — Institute Network
License to 10 IITs / NITs via campus sustainability procurement MoU.
Phase 3 (18-36 months) — B2B Channel
Partner with AC service companies (Daikin, Voltas, Blue Star dealers) as an add-on retrofit product.
Phase 4 (3+ years) — Consumer Retail
D2C via Amazon / Flipkart. Self-install kit format. Refill cartridge subscription (~Rs. 200/year).
Revenue model
Product sale + annual refill subscription. Institutional bulk pricing for colleges and housing societies.

## Slide 12
Team MEGHDOOT
School of Energy Science and Engineering | IIT Kharagpur
Vinay Arya
20ES91R07
Institute Post-Doctoral Fellow
vinayarya@kgpian.iitkgp.ac.in
Vikash Chandra
22ES92R03
PhD Scholar, SESE
vikash.es@kgpian.iitkgp.ac.in
Aman Kumar
25ES60R03
M.Tech Student, SESE
aman1825@kgpian.iitkgp.ac.in
Shivam Kumar
25ES60R11
M.Tech Student, SESE
kshivam511725@kgpian.iitkgp.ac.in
Mentor
Dr. Chirodeep Bakli | Associate Professor, SESE, IIT Kharagpur | cbakli@iitkgp.ac.in
SHEETAL is not just an idea — it is a thermodynamically grounded, low-cost, and passively scalable solution ready to begin deployment within IIT Kharagpur this academic year.